## Slide 1: How much energy did the outage cost?
WATT THE HACK 2026 · CHALLENGE 1
Rebuilding a wind park’s lost energy from its neighbours, with an honest uncertainty range
[Team name] · [Names]
Notes: About 5 seconds. Introduce the team in one breath and go straight to the problem.

## Slide 2: Park T is down for three days
THE PROBLEM
Park H
5 turbines
Wind measured
Park T
3 turbines
Wind unknown during the outage
Park O
2 turbines
Wind measured
The insurer asks: how many kWh did the outage cost? We rebuild T’s wind from H and O, convert it to power and add it up.
Watt The Hack 2026 · Judged outage: 1–3 Sep 2026, 432 ten-minute steps · 2 / 8
Notes: About 20 seconds. Park T, three turbines, is out for three days. The neighbouring parks H and O kept measuring. The insurer needs one number: the lost energy in kWh, and how sure we are. Our job: rebuild T’s wind speed from the neighbours, run it through the power curve and sum it up.

## Slide 3: One transparent formula per turbine
OUR MODEL
T = a + b · H + c · O
H, O = 1-hour average wind of each neighbouring park · a, b, c fitted on all data outside the outage
1-hour averages
Gusts at the neighbours are noise; trends carry over (agreement 0.80 → 0.89)
8 wind directions
a and b change with direction: T gets 84–93 % of H’s wind
No black box
Every coefficient can be printed and checked by the insurer
Watt The Hack 2026 · 3 / 8
Notes: About 30 seconds. The whole model is one line: T’s wind is a plus b times H’s wind plus c times O’s wind, one formula per turbine. Two refinements: we use 1-hour averages of the neighbours, because short gusts do not travel between parks, and a and b depend on the wind direction, because terrain lets T see between 84 and 93 percent of H’s wind. Everything can be printed and explained.

## Slide 4: Tested on 28 simulated outages, not one lucky week
INSIGHT 1
July
August
September
simulated 3-day outage, predicted blind
judged outage, 1–3 Sep
too little data
Official validation week alone
+0.1 %
Looked perfect, but only because T1 (+19 %) and T3 (−8 %) cancelled out
28 simulated outages, park energy error
11.0 % → 8.5 %
Baseline → our model; confirmed on 83 outages starting every day
Watt The Hack 2026 · 4 / 8
Notes: About 30 seconds. One validation week is luck. There the simple baseline looked perfect at plus 0.1 percent, but only because one turbine was 19 percent too high and another 8 percent too low. So we hid three days of park T at a time, 28 times across the summer, predicted each blind and compared with the truth. Over those 28 outages the baseline was off by 11 percent on average, our model by 8.5 percent. A repeat with an outage starting every day gave the same result.

## Slide 5: Average the power, not the wind
INSIGHT 2
4,500 kW full power
average power over the range
power at the best guess
0
5
10
wind speed, m/s
Average energy bias, baseline → our model
−8.5 % → +1.4 %
Between 3 and 11 m/s the curve bends upward: a gust above the guess adds more power than an equal lull removes.
So we average the power over the plausible wind range. Alone, this cut the park error from 11.0 % to 9.0 %.
Watt The Hack 2026 · Illustration: power curve of T1–T3 · 5 / 8
Notes: About 30 seconds. Our biggest single gain. The power curve bends upward exactly where most energy is made. If the wind is a bit higher than our guess, power rises a lot; if it is a bit lower, power drops less. So plugging in the single best guess systematically under-counts energy: the baseline was 8.5 percent too low on average. We average the power over the range of plausible wind speeds instead, which removes the bias: plus 1.4 percent, statistically zero.

## Slide 6: What remains is weather luck, so we show a range
INSIGHT 3
Baseline: too low on average (−8.5 %)
Our model: centred (+1.4 %); the ±11 % spread stays
−30 %
0
+30 %
Lost energy, judged outage 1–3 Sep
322 MWh
95 % range: 262–387 MWh
An outage’s energy error is its 3-day average wind error. Errors fade within hours and hit all three turbines at once.
Watt The Hack 2026 · One dot = one simulated 3-day outage · 6 / 8
Notes: About 30 seconds. Each dot is one simulated outage. The grey baseline sits mostly below zero: that bias is what we removed. What remains is the spread, about plus or minus 11 percent per outage. We found that an outage’s energy error is simply its three-day average wind error: errors fade within a few hours and all three turbines are wrong together, so nothing in the neighbour data can remove it. That is why we give the insurer a range: 322 megawatt hours for 1 to 3 September, between 262 and 387 with 95 percent confidence, a range built from 83 simulated outages.

## Slide 7: The transparent formula beat the black box
INSIGHT 4
Baseline formula
11.0 %
Gradient boosting (black box)
9.7 %
Small neural network
9.1 %
Our transparent formula
8.5 %, best
About 50 variants tested. Most extras (time weighting, time of day, temperature, pressure, curved fits) added numbers, not information.
Watt The Hack 2026 · Mean park energy error over 28 simulated outages, lower is better · 7 / 8
Notes: About 20 seconds. We also tried flexible models: gradient boosting and a small neural network. Both did worse than our one-line formula, and the black box’s uncertainty band was too narrow. Most other extras added nothing either. So explainability did not cost us accuracy: the transparent model is also the most accurate one.

## Slide 8: 322 MWh lost on 1–3 Sep, between 262 and 387 MWh
THE ANSWER
1
Tested on 28 simulated outages: park energy error 11.0 % → 8.5 %
2
Averaging the power removed the bias: −8.5 % → +1.4 %
3
One transparent formula, every number explainable, with an honest range
Try it live: [app URL] · upload any outage window, get kWh with a 95 % range
Notes: About 25 seconds. To sum up: tested on 28 simulated outages, the power fix removed the bias, and the remaining uncertainty is shown honestly as a range. For the judged outage that is 322 megawatt hours, between 262 and 387. Everything runs in our app: pick any outage window and get the lost energy with its range. Thank you.